## Mindigale WSS _Tender Docs
Tender for Rehabilitation of Midigale Water Supply System in Badhan District, Puntland
I/N | a | Unit | Quantity | Rate in USD | Amount in USD
A | 25 M3 CAPACITY & 12M-HIGH ELEVATED RCC RECTANGULAR WATER RESERVOIR
1 | Substructure Works for 25 cum capacity & 12m high elevated RCC rectangular water reservoir
1.1 | General cleaning for all broken stones, trees, sharps and other material which are occupying the area where is going to be build the elevated water tank . | M2 | 24
1.2 | Excavation of 6 footings of 1.4mx1.4m and 1.2m depth. Excavated material may be used backfilling for this pits after casting of the footings upon the approval by the engineer depending on the soil properties. | M3 | 34.656
1.3 | Lay 5cm thick Plain cement concrete of 1:3:6 mixing for column footings | M3 | 1.083
1.4 | Construct 120x120x50 cm reinforced concrete footing of 1:2:4 mixing ratio with # 6 Y14 both ways and column neck of 40x40cm and 1.5m high with # 6 Y 16 and stirrups of 8mm@ 150mm/cc. For 6 nos of column. | M3 | 7.71
1.5 | Re-fill and compact with pre excavated soil from the footing to the surrounding area of the columns neck's till the ground floor level. | M3 | 25.863
1.6 | 40cm thick stone masonary foundation with mixing ratio 1:4 | M3 | 3.84
1.7 | Construct 40cm wide, 20cm thick of reinforced concrete ground beam of 1:2:4 mixing ratio with # 6 Y16 and staffs of 8mm@ 150mm/cc over ground level. | M3 | 1.92
1.8 | 35cm thick Backfilling and well compact with pre excavated soil for floor level | M3 | 7.2
1.9 | Lay 5cm thick Plain cement concrete of 1:3:6 mixing for floor level | M3 | 1.2
2 | Superstructure Works
2.1 | Construct 6 R.C (1:2:4 Mixing ratio) columns of 40cm x 40cm and 3.5m height reinforced by No.6 Y16 and staffs of Ø 8mm @150mm c/c. | M3 | 5.376
2.2 | Construct 40cm wide, 50cm thick of reinforced concrete ring beams of 1:2:4 mixing ratio. The beams should be reinforced with # 6 Y14 and staffs of 8mm@ 150mm/cc. | M3 | 4.5
2.3 | Construct 30cm wide, 40cm thick of reinforced concrete loaded beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 8mm@ 150mm/cc. | M3 | 3.2
2.4 | Construct 6.4m length and 4.4m width R.C (1:2:4 Mixing ratio) slab base of 0.2m thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 150mm c/c. N.B The slab should mixed by machine, also it has to be kept moist and watered for a period of minimum 3 weeks and protect from sun | M3 | 5.6
2.5 | Construct RCC water retaining walls LM 20m (2x6m + 2x4m) and 2.2m height and 20cm thick to hold water (Water Barket walls) | M3 | 4.2
2.6 | Construct 6.0m length and 4.0m width RC (1:2:4 Mixing ratio) Cover slab with manhole and its cover. the slab should 0.15m thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 150mm c/c.the manhole size should be 50cmx60cm with cover N.B The slab should mixed by machine, also it has to be kept moist and watered for a period of minimum 3 weeks and protect from sun | M3 | 4.224
2.7 | Apply two coats of Plastering internal and external walls of the water holding section of the tank with a ratio of 1:2:4 | M2 | 76
2.8 | Apply White wash and destemper on the external walls of the tank | M2 | 84.96
2.9 | Provide and fix internal and external 12m and 2m height respectively 2"GI pipe ladder to top of water tank. | Item | 1
| Sub-total A _ 25m3 & 12m-high Elevated Water Tank |  |  |  | 0
I/N | Description of Work/Activities | Unit | Quantity | Rate in USD | Amount in USD
B | SHALLOW WELL WORKS
3 | Drilling/Deepening of two shallow wells
3.1 | Drill the shallow well up to 20 meters depth, well-1 from 4m to 20 meters | m | 24 |  | 0
3.2 | Drill the shallow well up to 15 meters depth, well-2 from 6m to 15 meters | m | 13.5 |  | 0
| Sub-total B _ Shallow Well Works |  |  |  | 0
I/N | Description of Work/Activities | Unit | Quantity | Rate in USD | Amount in USD
C | Pipeline Works
4 | Distribution network pipeline (2650m)
4.1 | Excavation of trench line for installation of 2" HDPE PN10 Class B pipeline at the mean depth of 50 cm x 0.30m width x2650m long, Inclusive proper anchor beds all along the pipe line | m3 | 397.5
4.2 | Supply of Ø 2" HDPE PN10 Class B 2000 m long Distribution network buried at 0.50 m below ground from the new 25cums elevated tank to the village inclusive with necessary fittings | Lm | 2000
4.3 | Install Ø 2" HDPE PN10 Class B transmission pipe from the shallow well to the new 25 cums elevated water, inclusively with necessary fittings line and also fix and protect the pipe with a bed and cover layer of silt sand compacted at 85 Proctor complete | Lm | 650
4.4 | With the relicts of excavation back fill the trench complete | Lm | 2650
Inlet pipe, Overflow pipe, Air vint pipe, Drain pipe and Standing pipe fittings
4.5 | DN 2", PN6, male threaded GI Nipple | No | 8
4.6 | DN 2" PN6, GI Tee | No | 14
4.7 | DN 2", PN, female threaded GI 90o deg bend | No | 12
4.8 | DN 2" PN6, female threaded GI Union | No | 6
4.9 | DN 2" PN6, DCI gate valve, female threaded | No | 2
4.1 | DN 2", class B GI pipe, 6 m long, both ends male threaded, complete with female threaded couplings | m | 30
4.11 | Riser pipes Ø 2" HDPE PN15 Class c inclusive with necessary fittings | pcs | 9
4.12 | Installation labor costs, testing and commissioning. | Ls | 1
| Sub-total C _ Pipeline Works |  |  |  | 0
I/N | Description of Work/Activities | Unit | Quantity | Rate in USD | Amount in USD
D | SOLAR INSTALLATION AND SUBMERSIBLE PUMP WORK
5 | Solar Power Supply & Installation
5.1 | Procure and install Solar Panels Germany or CE-certified Monocrystalline solar panels with Min. Panel power rating 450W, with manufacturer’s datasheet. A Total Peak power of 11.25 kW: powering the pump and controller, approved by the Engineer. | No. | 25
5.2 | Aluminium PV Mounting Structure with the smaller height of the structure not to be less than 1M, approved by the Engineer. | No. | 25
5.3 | Required RCC concrete foundation for the Aluminum PV Mounting Structure should have a dimension of length 400mm by width 400mm by depth 700mm (below G.L), and 300mm above ground level. | LS | 2
6 | Submersible Pump
6.1 | 4kW Varuna submersible pump complete with motor, flanges, non-return valve and other relevant accessories with a Flow Range of 260 LPM, Head 80m (Minimum), , approved by the Engineer. | Unit | 2
6.2 | Pump controller complete with accessories (Hobsolar 8kW or equivalent), approved by the Engineer. | Unit | 2
6.3 | PV Disconnect Switch 1000v/40A/DC MCB | Unit | 2
6.4 | Supply of lightning spike arrestor in copper c/w accessories i.e., GI Pipes, Conductor c/w accessories i.e., GI Pipes, Conductor cable/copper tape etc. | Lsm | 2
6.5 | Submersible drop cable 4x6mm2 felxible for the pump | m | 150
6.6 | Splicing Kit for the submersible cable | No | 2
6.7 | DC 1x6mm DC cable for the PV panels | m | 100
6.8 | Electrical sundries for the installation- to include earth rod; earth lead cable and clamping device, adaptor metal box and other accessories. | Lsm | 1
| Sub-total D _ Solar System & Submersible Pump |  |  |  | 0
I/N | Description of Work/Activities | Unit | Quantity | Rate in USD | Amount in USD
E | FENCING WORKS
7 | Construction of 50 meters steel Chainlink fence
7.1 | Excavate 40 No 0.8m deep, by 0.3m square holes to fix concrete pillar bases | No. | 40
7.2 | Supply broken stones 75mm - 100mm and fill into the holes above and ram properly to a depth of 0.3min the 40No. holes for the fence posts. | M3 | 3.9
7.3 | Supply cement, sand, gravel and clean water and labour and mix at ratio of 1:3:6 (cement:sand:gravel) and lay to make blinding concrete 50mm thick layer for the 40 No holes for the fence posts. Cure for 1 day by keeping the concrete wet by pouring water in the morning and in the late afternoon. | M3 | 0.2
7.4 | Supply cement, sand, gravel and clean water and labour and mix at ratio of 1:2:4 (cement:sand:gravel) and lay to make 40 No, 0.3m square and 0.5m deep concrete column bases to fix steel posts. Cure for 7 days by keeping the concrete wet by pouring water in the morning and in the late afternoon. | M3 | 4
7.5 | Supply and fix 40 No, 75mm steel angle bars 4 mm thick and 2.3m long into the concrete columns item 1.2 above to form fence posts. 0.3m length shall be embedded into the concrete column bases. The angle iron will be painted with oil based paint (green clour 3 coats) after fixing. | M | 96
7.6 | Supply and fix 4 pieces of 20m long, 2m high, 3mm diameter galvanized steel chainlink on the steel posts erected in item 1.3 above. The chainlink shall be tied firmly with steel binding wire to the steel posts at 5 intervals as 0m, 0.5m, 1m,1.5m and 2m above the ground level. | M2 | 80
7.7 | Supply materials (3mm mild steel sheet (6m2), 50mm by 4mm thick square hollow tube (12m), 150mm by 4mm thick square hollow tube (5.7m in two equal length pieces, cut weld and fix to make a gate 2.44m wide and 2,44mm high to the fence. Cost to include 600mm by 600mm square and 800mm deep 1:2:4 mass concrete column to fix the two 200mm gate support hollow tube with 400mm of the 200mm embedded into the concrete | No | 1
| Sub-total E _ Fencing Works |  |  |  | 0
SUMMARY PAGE - REHAB OF MINDIGALE WATER SUPPLY SYSTEM (Badhan, Puntland) |  |  | QTY | SUM | TOTAL SUM
A | Sub-total A _ 25m3 & 12m-high Elevated Water Tank |  | 1 | 1
B | Sub-total B _ Shallow Well Works |  | 1 | 1
C | Sub-total C _ Pipeline Works |  | 1 | 1
D | Sub-total D _ Solar System & Submersible Pump |  | 1 | 1
E | Sub-total E _ Fencing Works |  | 1 | 1
GRAND TOTAL FOR MINDIGALE WSS REHAB
(CONTRACTOR) …………………………………………………………………………………
Signature: …………………………………………………………………………………….............
Address: …………………………………………………………………………………….............
Tel No: ………………………………………………………………………………………….........
Date: ……………………………………………………………………………………………………
Stamp: